Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Buckaroos, Inc. ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text, and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA). Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Buckaroos, Inc., 9635 Park Davis Dr., Indianapolis, IN 46235; Phone: (800) 969-3113; Website: www.buckaroos.com; Email: info@buckaroos.com.

For information about MasterSpec, contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 220529 - HANGERS AND SUPPORTS FOR PLUMBING PIPING AND EQUIPMENT

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Metal pipe hangers and supports.

Trapeze pipe hangers.

Fiberglass pipe hangers.

Metal framing systems.

Fiberglass strut systems.

Insulated pipe support systems.

Fastener systems.

Pipe stands.

Pipe positioning systems.

Equipment supports.

Related Sections:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 055000 "Metal Fabrications" for structural-steel shapes and plates for trapeze hangers for pipe and equipment supports.

Section 220516 "Expansion Fittings and Loops for Plumbing Piping" for pipe guides and anchors.

[Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment"] [Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment"] for vibration isolation devices.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

MSS: Manufacturers Standardization Society of The Valve and Fittings Industry Inc.

PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

Delegated Design: Design trapeze pipe hangers and equipment supports, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Structural Performance: Hangers and supports for plumbing piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated according to [ASCE/SEI 7] <Insert requirement>.

Design supports for multiple pipes, including pipe stands, capable of supporting combined weight of supported systems, system contents, and test water.

Design equipment supports capable of supporting combined operating weight of supported equipment and connected systems and components.

Design seismic-restraint hangers and supports for piping and equipment[ and obtain approval from authorities having jurisdiction].

ACTION SUBMITTALS

Product Data: For each type of product indicated.

Shop Drawings:[ Signed and sealed by a qualified professional engineer.] Show fabrication and installation details and include calculations for the following; include Product Data for components:

Trapeze pipe hangers.

Metal framing systems.

Fiberglass strut systems.

Pipe stands.

Equipment supports.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

Delegated-Design Submittal: For trapeze hangers indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Detail fabrication and assembly of trapeze hangers.

Design Calculations: Calculate requirements for designing trapeze hangers.

INFORMATIONAL SUBMITTALS

Welding certificates.

QUALITY ASSURANCE

Retain both paragraphs below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

Structural Steel Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

Pipe Welding Qualifications: Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

METAL PIPE HANGERS AND SUPPORTS

Carbon-Steel Pipe Hangers and Supports:

Description: MSS SP-58, Types 1 through 58, factory-fabricated components.

Galvanized Metallic Coatings: Pregalvanized or hot dipped.

Nonmetallic Coatings: Plastic coating, jacket, or liner.

Padded Hangers: Hanger with fiberglass or other pipe insulation pad or cushion to support bearing surface of piping.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Stainless-Steel Pipe Hangers and Supports:

Description: MSS SP-58, Types 1 through 58, factory-fabricated components.

Padded Hangers: Hanger with fiberglass or other pipe insulation pad or cushion to support bearing surface of piping.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [stainless steel] <Insert material>.

Copper Pipe Hangers:

Manufacturers' catalogs indicate that copper pipe hangers are small, typically NPS 4 (DN 100) or smaller, and types available are limited.

Description: MSS SP-58, Types 1 through 58, copper-coated-steel, factory-fabricated components.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [copper-coated steel] [stainless steel] <Insert material>.

TRAPEZE PIPE HANGERS

Trapeze pipe hanger in paragraph below requires calculating and detailing at each use.

Description: MSS SP-69, Type 59, shop- or field-fabricated pipe-support assembly made from structural carbon-steel shapes with MSS SP-58 carbon-steel hanger rods, nuts, saddles, and U-bolts.

FIBERGLASS PIPE HANGERS

Clevis-Type, Fiberglass Pipe Hangers:

Description: Similar to MSS SP-58, Type 1, steel pipe hanger except hanger is made of fiberglass or fiberglass-reinforced resin.

Hanger rods in subparagraph below are typically stainless steel.

Hanger Rods: Continuous-thread rod, washer, and nuts made of [fiberglass] [polyurethane] [or] [stainless steel] <Insert material>.

Strap-Type, Fiberglass Pipe Hangers:

Description: Similar to MSS SP-58, Type 9 or Type 10, steel pipe hanger except hanger is made of fiberglass-reinforced resin.

Hanger rods and attachments in subparagraph below are typically stainless steel.

Hanger Rod and Fittings: Continuous-thread rod, washer, and nuts made of [stainless steel] <Insert material>.

METAL FRAMING SYSTEMS

Metal framing systems in this article require calculating and detailing at each use.

Framing systems in first paragraph below are made by MFMA members.

MFMA Manufacturer Metal Framing Systems:

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

B-line, an Eaton business.

Flex-Strut Inc.

G-Strut.

Haydon Corporation.

Thomas & Betts Corporation; A Member of the ABB Group.

Unistrut; Part of Atkore International.

Wesanco, Inc.

<Insert manufacturer's name>.

Description: Shop- or field-fabricated pipe-support assembly for supporting multiple parallel pipes.

Standard: MFMA-4.

Channels: Continuous slotted steel channel with inturned lips.

Channel Nuts: Formed or stamped steel nuts or other devices designed to fit into channel slot and, when tightened, prevent slipping along channel.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Retain one of four subparagraphs below for coating.

Metallic Coating: [Electroplated zinc] [Hot-dipped galvanized] [Mill galvanized] [In-line, hot galvanized] [Mechanically-deposited zinc].

Paint Coating: [Vinyl] [Vinyl alkyd] [Epoxy] [Polyester] [Acrylic] [Amine] [Alkyd] <Insert paint type>.

Plastic Coating: [PVC] [Polyurethane] [Epoxy] [Polyester] <Insert plastic type>.

Combination Coating: <Insert coating materials in order of application>.

Framing systems in paragraph below should be equal to or able to exceed MFMA-4 requirements.

Non-MFMA Manufacturer Metal Framing Systems:

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Anvil International.

Empire Industries, Inc.

ERICO International Corporation.

PHD Manufacturing, Inc.

<Insert manufacturer's name>.

Description: Shop- or field-fabricated pipe-support assembly made of steel channels, accessories, fittings, and other components for supporting multiple parallel pipes.

Standard: Comply with MFMA-4.

Channels: Continuous slotted steel channel with inturned lips.

Channel Nuts: Formed or stamped steel nuts or other devices designed to fit into channel slot and, when tightened, prevent slipping along channel.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Coating: [Zinc] [Paint] [PVC] <Insert coating>.

FIBERGLASS STRUT SYSTEMS

Fiberglass strut systems in this article require calculating and detailing at each use.

Retain "Manufacturers" Paragraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Champion Fiberglass, Inc.

Seasafe, Inc.; AMICO, a Gibraltar Industries Company.

<Insert manufacturer's name>.

Description: Shop- or field-fabricated pipe-support assembly similar to MFMA-4 for supporting multiple parallel pipes.

Channels: Continuous slotted fiberglass[ or other plastic] channel with inturned lips.

Channel Nuts: Fiberglass nuts or other devices designed to fit into channel slot and, when tightened, prevent slipping along channel.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [fiberglass] [stainless steel] <Insert material>.

INSULATED PIPE SUPPORT SYSTEMS

Buckaroos, Inc.'s "CoolDry™ Insulated Saddles" allow for additional lineal movement to help avoid compromising the insulation integrity. Insulation can fail due to thermal expansion and contraction in the piping system. This system is an excellent application at the clevis or strut support location for insulated piping systems that anticipates thermal expansion and start up movement. CoolDry™ logo sticker is located on bottom for visual inspection and verification at every support location.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Buckaroos, Inc.; CoolDry™ Insulated Saddles, Heavy Duty CoolDry™ Insulated Saddles, and CoolDry™ Insulated Sliding Saddles, or comparable product by one of the following:

Buckaroos, Inc.

Carpenter & Paterson, Inc.

Clement Support Services.

<Insert manufacturer's name>.

Insulation Material for Cold or Hot Piping, from Minus 40 to Plus 275 Deg F (Minus 40 to Plus 125 Deg C): Naturally hydrophobic rigid phenolic foam. Comply with ASTM C 1126, Type III.

Flame-spread index of 25 or less and smoke-developed index of 50 or less as tested by ASTM E 84.

Thermal Properties, NPS 10 (DN 250) and Smaller: 3.75-lb/cu. ft. (60-kg/cu. m) nominal density, and thermal conductivity (k-value) not to exceed 0.17 Btu x in./h x sq. ft. x deg F (0.0245 W/m x K) at 75 deg F (24 deg C) according to ASTM C 518.

Thermal Properties, NPS 12 to NPS 30 (DN 300 to DN 750): 5.0-lb/cu. ft. (80-kg/cu. m) nominal density, and thermal conductivity (k-value) not to exceed 0.2 Btu x in./h x sq. ft. x deg F (0.0288 W/m x K) at 75 deg F (24 deg C) according to ASTM C 518.

Vapor Barrier: ASTM C 1136, Type IX, three-ply composite membrane consisting of a 0.5-mil (0.013-mm) white polyester film, 1.0-mil (0.025-mm) aluminum foil, and one 0.5-mil (0.013-mm) clear polyester film.

Flame-spread index of 25 or less and smoke-developed index of 50 or less as tested by ASTM E 84.

Water-Vapor Permeance: ASTM E 96/E 96M, Procedure B, zero-permeance (zero metric permeance) abuse-resistant vapor barrier jacket with 1-1/2-inch- (38-mm-) wide longitudinal pressure-sensitive acrylic tape closure system.

See Part 3 for application and installation information. For clevis or band hangers use Buckaroos' "CoolDry™ Insulated Saddles." IMPORTANT: For insulated piping, install insulated pipe support systems when setting the piping elevation.

Insulation Protection Shields: Galvanized metal, G90 (Z275) coating designation, complying with ASTM A 653/A 653M, 180-degree saddle, centered and adhered to bottom a minimum of 1-1/2 inches (38 mm) for jacketed insulation extending from each side to allow for proper circumferential closure at butt joints with 3-inch- (76-mm-) wide zero-permeance (zero metric permeance) tape.

For trapeze or clamped systems use Buckaroos' "Heavy Duty CoolDry™ Insulated Saddles." Use an additional 180-degree G90 (Z275) galvanized shield for top of support if clamping is required.

Heavy Duty Insulation Protection Shields: Galvanized metal, 12-gage, G90 (Z275) coating designation, complying with ASTM A 653/A 653M, 180-degree saddle, centered and adhered to bottom a minimum of 1-1/2 inches (38 mm) jacketed insulation extending from each side to allow for proper circumferential closure at butt joints with 3-inch- (76-mm-) wide zero-permeance (zero metric permeance) tape. Structural steel plate welded to bottom of galvanized shield for sizes NPS 6 (DN 150) and larger.

For support locations subject to linear expansion and contraction use Buckaroos' "CoolDry™ Insulated Sliding Saddles."

Sliding Protection Shield: Galvanized metal, G90 (Z275) coating designation, complying with ASTM A 653/A 653M, ribbed, with PTFE layer on top. Ribbed shield is 4 inches (100 mm) shorter and centered below primary protection shield. Allows for 2 inches (50 mm) of lateral movement to account for linear expansion or contraction.

Saddle Label: Manufacturer's saddle label with logo sticker to be visible for verification of proper installation.

FASTENER SYSTEMS

Verify suitability of fasteners in this article for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

Powder-Actuated Fasteners: Threaded-steel stud, for use in hardened portland cement concrete with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

Mechanical-Expansion Anchors: Insert-wedge-type, [zinc-coated ] [stainless-]steel anchors, for use in hardened portland cement concrete; with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

PIPE STANDS

Pipe stands in this article require calculating and detailing at each use.

General Requirements for Pipe Stands: Shop- or field-fabricated assemblies made of manufactured corrosion-resistant components to support roof-mounted piping.

Compact Pipe Stand: One-piece plastic unit with integral-rod roller, pipe clamps, or V-shaped cradle to support pipe, for roof installation without membrane penetration.

Low-Type, Single-Pipe Stand: One-piece [plastic] [stainless-steel] base unit with plastic roller, for roof installation without membrane penetration.

High-Type, Single-Pipe Stand:

Description: Assembly of base, vertical and horizontal members, and pipe support, for roof installation without membrane penetration.

Base: [Plastic] [Stainless steel].

Vertical Members: Two or more cadmium-plated-steel or stainless-steel, continuous-thread rods.

Horizontal Member: Cadmium-plated-steel or stainless-steel rod with plastic or stainless-steel, roller-type pipe support.

High-Type, Multiple-Pipe Stand:

Description: Assembly of bases, vertical and horizontal members, and pipe supports, for roof installation without membrane penetration.

Bases: One or more; plastic.

Vertical Members: Two or more protective-coated-steel channels.

Horizontal Member: Protective-coated-steel channel.

Pipe Supports: Galvanized-steel, clevis-type pipe hangers.

Curb-Mounting-Type Pipe Stands: Shop- or field-fabricated pipe supports made from structural-steel shapes, continuous-thread rods, and rollers, for mounting on permanent stationary roof curb.

PIPE POSITIONING SYSTEMS

Description: IAPMO PS 42, positioning system of metal brackets, clips, and straps for positioning piping in pipe spaces; for plumbing fixtures in commercial applications.

EQUIPMENT SUPPORTS

Equipment support in paragraph below requires calculating and detailing at each use.

Description: Welded, shop- or field-fabricated equipment support made from structural carbon-steel shapes.

MISCELLANEOUS MATERIALS

Structural Steel: ASTM A 36/A 36M, carbon-steel plates, shapes, and bars; black and galvanized.

Grout: ASTM C 1107, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink and nonmetallic grout; suitable for interior and exterior applications.

Properties: Nonstaining, noncorrosive, and nongaseous.

Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

EXECUTION

HANGER AND SUPPORT INSTALLATION

Metal Pipe-Hanger Installation: Comply with MSS SP-69 and MSS SP-89. Install hangers, supports, clamps, and attachments as required to properly support piping from the building structure.

Trapeze pipe hanger in first paragraph below requires calculating and detailing at each use.

Metal Trapeze Pipe-Hanger Installation: Comply with MSS SP-69 and MSS SP-89. Arrange for grouping of parallel runs of horizontal piping, and support together on field-fabricated trapeze pipe hangers.

Pipes of Various Sizes: Support together and space trapezes for smallest pipe size or install intermediate supports for smaller diameter pipes as specified for individual pipe hangers.

Field fabricate from ASTM A 36/A 36M, carbon-steel shapes selected for loads being supported. Weld steel according to AWS D1.1/D1.1M.

Fiberglass Pipe-Hanger Installation: Comply with applicable portions of MSS SP-69 and MSS SP-89. Install hangers and attachments as required to properly support piping from building structure.

Metal framing system in first paragraph below requires calculating and detailing at each use.

Metal Framing System Installation: Arrange for grouping of parallel runs of piping, and support together on field-assembled metal framing systems.

Fiberglass strut system in first paragraph below requires calculating and detailing at each use.

Fiberglass Strut System Installation: Arrange for grouping of parallel runs of piping, and support together on field-assembled fiberglass struts.

For product information on insulated pipe support systems, see "Insulated Pipe Support Systems" Article and coordinate with "Insulated Pipe Support System Installation" Paragraph below.

Insulated Pipe Support System Installation: Install insulated pipe support system during the piping system installation, prior to applying pipe insulation. Install while setting the piping elevation. Install according to manufacturer's written instructions.

For Clevis or Band Hangers: Install insulated pipe support system with insulation protection shields.

For Trapeze or Clamped Systems: Install insulated pipe support system with heavy-duty insulation protection shields. Install additional 180-degree galvanized shield for top of support if clamping is required.

For Support Locations Subject to Linear Expansion and Contraction: Install insulated pipe support system with sliding protection shields.

Position manufacturer's saddle label and logo sticker to be visible for verification of proper installation.

Fastener System Installation:

Verify suitability of fasteners in two subparagraphs below for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

Install powder-actuated fasteners for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick in concrete after concrete is placed and completely cured. Use operators that are licensed by powder-actuated tool manufacturer. Install fasteners according to powder-actuated tool manufacturer's operating manual.

Install mechanical-expansion anchors in concrete after concrete is placed and completely cured. Install fasteners according to manufacturer's written instructions.

Pipe stand in first paragraph below requires calculating and detailing at each use.

Pipe Stand Installation:

Pipe Stand Types except Curb-Mounted Type: Assemble components and mount on smooth roof surface. Do not penetrate roof membrane.

Curb-Mounted-Type Pipe Stands: Assemble components or fabricate pipe stand and mount on permanent, stationary roof curb. See Section 077200 "Roof Accessories" for curbs.

Pipe Positioning-System Installation: Install support devices to make rigid supply and waste piping connections to each plumbing fixture.

Install hangers and supports complete with necessary attachments, inserts, bolts, rods, nuts, washers, and other accessories.

Equipment support in first paragraph below requires calculating and detailing at each use.

Equipment Support Installation: Fabricate from welded-structural-steel shapes.

Install hangers and supports to allow controlled thermal and seismic movement of piping systems, to permit freedom of movement between pipe anchors, and to facilitate action of expansion joints, expansion loops, expansion bends, and similar units. Install insulated pipe support system with sliding saddles to account for up to 2 inches (50 mm) of linear expansion or contraction.

Install lateral bracing with pipe hangers and supports to prevent swaying.

Install building attachments within concrete slabs or attach to structural steel. Install additional attachments at concentrated loads, including valves, flanges, and strainers, [NPS 2-1/2 (DN 65)] <Insert pipe size> and larger and at changes in direction of piping. Install concrete inserts before concrete is placed; fasten inserts to forms and install reinforcing bars through openings at top of inserts.

Load Distribution: Install hangers and supports so that piping live and dead loads and stresses from movement will not be transmitted to connected equipment.

Pipe Slopes: Install hangers and supports to provide indicated pipe slopes and to not exceed maximum pipe deflections allowed by ASME B31.9 for building services piping. For insulated piping, install insulated pipe support systems when setting the piping elevation.

Insulated Piping:

Specify parts in subparagraph below as galvanized or painted, as required. Other materials are available in place of wooden blocks.

Attach clamps and spacers to piping.

Piping Operating above Ambient Air Temperature: Clamp may project through insulation.

Piping Operating below Ambient Air Temperature: Use insulated pipe support system to match OD of insert.

Do not exceed pipe stress limits allowed by ASME B31.9 for building services piping.

EQUIPMENT SUPPORTS

Fabricate structural-steel stands to suspend equipment from structure overhead or to support equipment above floor.

Grouting: Place grout under supports for equipment and make bearing surface smooth.

Provide lateral bracing, to prevent swaying, for equipment supports.

METAL FABRICATIONS

Cut, drill, and fit miscellaneous metal fabrications for [trapeze pipe hangers] [and] [equipment supports].

Fit exposed connections together to form hairline joints. Field weld connections that cannot be shop welded because of shipping size limitations.

Field Welding: Comply with AWS D1.1/D1.1M procedures for shielded, metal arc welding; appearance and quality of welds; and methods used in correcting welding work; and with the following:

Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

Obtain fusion without undercut or overlap.

Remove welding flux immediately.

Finish welds at exposed connections so no roughness shows after finishing and so contours of welded surfaces match adjacent contours.

ADJUSTING

Hanger Adjustments: Adjust hangers to distribute loads equally on attachments and to achieve indicated slope of pipe.

Trim excess length of continuous-thread hanger and support rods to [1-1/2 inches (40 mm)] <Insert dimension>.

PAINTING

Retain first "Touchup" Paragraph below if Section 099113 "Exterior Painting" or Section 099123 "Interior Painting" is not in Project Manual.

Touchup: Clean field welds and abraded areas of shop paint. Paint exposed areas immediately after erecting hangers and supports. Use same materials as used for shop painting. Comply with SSPC-PA 1 requirements for touching up field-painted surfaces.

Apply paint by brush or spray to provide a minimum dry film thickness of 2.0 mils (0.05 mm).

Retain "Touchup" Paragraph below if Section 099113 "Exterior Painting" or Section 099123 "Interior Painting" is in Project Manual. Revise reference if Section 099600 "High-Performance Coatings" applies instead.

Touchup: Cleaning and touchup painting of field welds, bolted connections, and abraded areas of shop paint on miscellaneous metal are specified in [Section 099113 "Exterior Painting."] [Section 099123 "Interior Painting."] [Section 099600 "High-Performance Coatings."]

Galvanized Surfaces: Clean welds, bolted connections, and abraded areas and apply galvanizing-repair paint to comply with ASTM A 780.

HANGER AND SUPPORT SCHEDULE

Specific hanger and support requirements are in Sections specifying piping systems and equipment.

Comply with MSS SP-69 for pipe-hanger selections and applications that are not specified in piping system Sections.

Use hangers and supports with galvanized metallic coatings for piping and equipment that will not have field-applied finish.

Use nonmetallic coatings on attachments for electrolytic protection where attachments are in direct contact with copper tubing.

Use carbon-steel [pipe hangers and supports] [metal trapeze pipe hangers] [and] [metal framing systems] and attachments for general service applications.

Use [stainless-steel pipe hangers] [and] [fiberglass pipe hangers] [and] [fiberglass strut systems] and [stainless-steel] [or] [corrosion-resistant] attachments for hostile environment applications.

Use copper-plated pipe hangers and [copper] [or] [stainless-steel] attachments for copper piping and tubing.

Use padded hangers for piping that is subject to scratching.

Use insulated pipe support system for insulated piping and tubing.

Horizontal-Piping Hangers and Supports: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Adjustable, Steel Clevis Hangers (MSS Type 1): For suspension of noninsulated or insulated, stationary pipes NPS 1/2 to NPS 30 (DN 15 to DN 750).

Yoke-Type Pipe Clamps (MSS Type 2): For suspension of up to 1050 deg F (566 deg C), pipes NPS 4 to NPS 24 (DN 100 to DN 600), requiring up to 4 inches (100 mm) of insulation.

Carbon- or Alloy-Steel, Double-Bolt Pipe Clamps (MSS Type 3): For suspension of pipes NPS 3/4 to NPS 36 (DN 20 to DN 900), requiring clamp flexibility and up to 4 inches (100 mm) of insulation.

Steel Pipe Clamps (MSS Type 4): For suspension of cold and hot pipes NPS 1/2 to NPS 24 (DN 15 to DN 600) if little or no insulation is required.

Pipe Hangers (MSS Type 5): For suspension of pipes NPS 1/2 to NPS 4 (DN 15 to DN 100), to allow off-center closure for hanger installation before pipe erection.

Adjustable, Swivel Split- or Solid-Ring Hangers (MSS Type 6): For suspension of noninsulated, stationary pipes NPS 3/4 to NPS 8 (DN 20 to DN 200).

Adjustable, Steel Band Hangers (MSS Type 7): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Adjustable Band Hangers (MSS Type 9): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Adjustable, Swivel-Ring Band Hangers (MSS Type 10): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Split Pipe Ring with or without Turnbuckle Hangers (MSS Type 11): For suspension of noninsulated, stationary pipes NPS 3/8 to NPS 8 (DN 10 to DN 200).

Extension Hinged or Two-Bolt Split Pipe Clamps (MSS Type 12): For suspension of noninsulated, stationary pipes NPS 3/8 to NPS 3 (DN 10 to DN 80).

U-Bolts (MSS Type 24): For support of heavy pipes NPS 1/2 to NPS 30 (DN 15 to DN 750).

Clips (MSS Type 26): For support of insulated pipes not subject to expansion or contraction.

Pipe Saddle Supports (MSS Type 36): For support of pipes NPS 4 to NPS 36 (DN 100 to DN 900), with steel-pipe base stanchion support and cast-iron floor flange or carbon-steel plate.

Pipe Stanchion Saddles (MSS Type 37): For support of pipes NPS 4 to NPS 36 (DN 100 to DN 900), with steel-pipe base stanchion support and cast-iron floor flange or carbon-steel plate, and with U-bolt to retain pipe.

Adjustable Pipe Saddle Supports (MSS Type 38): For stanchion-type support for pipes NPS 2-1/2 to NPS 36 (DN 65 to DN 900) if vertical adjustment is required, with steel-pipe base stanchion support and cast-iron floor flange.

Single-Pipe Rolls (MSS Type 41): For suspension of pipes NPS 1 to NPS 30 (DN 25 to DN 750), from two rods if longitudinal movement caused by expansion and contraction might occur.

Insulated Sliding Saddle Pipe Supports: For suspension of pipes NPS 3-1/2 to NPS 24 (DN 90 to DN 600), from single rod if horizontal movement caused by expansion and contraction might occur.

Adjustable Roller Hangers (MSS Type 43): For suspension of pipes NPS 2-1/2 to NPS 24 (DN 65 to DN 600), from single rod if horizontal movement caused by expansion and contraction might occur.

Complete Pipe Rolls (MSS Type 44): For support of pipes NPS 2 to NPS 42 (DN 50 to DN 1050) if longitudinal movement caused by expansion and contraction might occur but vertical adjustment is not necessary.

Pipe Roll and Plate Units (MSS Type 45): For support of pipes NPS 2 to NPS 24 (DN 50 to DN 600) if small horizontal movement caused by expansion and contraction might occur and vertical adjustment is not necessary.

Adjustable Pipe Roll and Base Units (MSS Type 46): For support of pipes NPS 2 to NPS 30 (DN 50 to DN 750) if vertical and lateral adjustment during installation might be required in addition to expansion and contraction.

Vertical-Piping Clamps: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Extension Pipe or Riser Clamps (MSS Type 8): For support of pipe risers NPS 3/4 to NPS 24 (DN 24 to DN 600).

Carbon- or Alloy-Steel Riser Clamps (MSS Type 42): For support of pipe risers NPS 3/4 to NPS 24 (DN 20 to DN 600) if longer ends are required for riser clamps.

Hanger-Rod Attachments: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Steel Turnbuckles (MSS Type 13): For adjustment up to 6 inches (150 mm) for heavy loads.

Steel Clevises (MSS Type 14): For 120 to 450 deg F (49 to 232 deg C) piping installations.

Swivel Turnbuckles (MSS Type 15): For use with MSS Type 11, split pipe rings.

Malleable-Iron Sockets (MSS Type 16): For attaching hanger rods to various types of building attachments.

Steel Weldless Eye Nuts (MSS Type 17): For 120 to 450 deg F (49 to 232 deg C) piping installations.

Building Attachments: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Steel or Malleable Concrete Inserts (MSS Type 18): For upper attachment to suspend pipe hangers from concrete ceiling.

Top-Beam C-Clamps (MSS Type 19): For use under roof installations with bar-joist construction, to attach to top flange of structural shape.

Side-Beam or Channel Clamps (MSS Type 20): For attaching to bottom flange of beams, channels, or angles.

Center-Beam Clamps (MSS Type 21): For attaching to center of bottom flange of beams.

Welded Beam Attachments (MSS Type 22): For attaching to bottom of beams if loads are considerable and rod sizes are large.

C-Clamps (MSS Type 23): For structural shapes.

Top-Beam Clamps (MSS Type 25): For top of beams if hanger rod is required tangent to flange edge.

Side-Beam Clamps (MSS Type 27): For bottom of steel I-beams.

Steel-Beam Clamps with Eye Nuts (MSS Type 28): For attaching to bottom of steel I-beams for heavy loads.

Linked-Steel Clamps with Eye Nuts (MSS Type 29): For attaching to bottom of steel I-beams for heavy loads, with link extensions.

Malleable-Beam Clamps with Extension Pieces (MSS Type 30): For attaching to structural steel.

Welded-Steel Brackets: For support of pipes from below or for suspending from above by using clip and rod. Use one of the following for indicated loads:

Light (MSS Type 31): 750 lb (340 kg).

Medium (MSS Type 32): 1500 lb (680 kg).

Heavy (MSS Type 33): 3000 lb (1360 kg).

Side-Beam Brackets (MSS Type 34): For sides of steel or wooden beams.

Plate Lugs (MSS Type 57): For attaching to steel beams if flexibility at beam is required.

Horizontal Travelers (MSS Type 58): For supporting piping systems subject to linear horizontal movement where headroom is limited.

Saddles and Shields: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Insulated Pipe Support Systems: For supporting insulated pipe.

Spring Hangers and Supports: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Restraint-Control Devices (MSS Type 47): Where indicated to control piping movement.

Spring Cushions (MSS Type 48): For light loads if vertical movement does not exceed 1-1/4 inches (32 mm).

Spring-Cushion Roll Hangers (MSS Type 49): For equipping Type 41, roll hanger with springs.

Spring Sway Braces (MSS Type 50): To retard sway, shock, vibration, or thermal expansion in piping systems.

Variable-Spring Hangers (MSS Type 51): Preset to indicated load and limit variability factor to 25 percent to allow expansion and contraction of piping system from hanger.

Variable-Spring Base Supports (MSS Type 52): Preset to indicated load and limit variability factor to 25 percent to allow expansion and contraction of piping system from base support.

Variable-Spring Trapeze Hangers (MSS Type 53): Preset to indicated load and limit variability factor to 25 percent to allow expansion and contraction of piping system from trapeze support.

Constant Supports: For critical piping stress and if necessary to avoid transfer of stress from one support to another support, critical terminal, or connected equipment. Include auxiliary stops for erection, hydrostatic test, and load-adjustment capability. These supports include the following types:

Horizontal (MSS Type 54): Mounted horizontally.

Vertical (MSS Type 55): Mounted vertically.

Trapeze (MSS Type 56): Two vertical-type supports and one trapeze member.

Comply with MSS SP-69 for trapeze pipe-hanger selections and applications that are not specified in piping system Sections.

Comply with MFMA-103 for metal framing system selections and applications that are not specified in piping system Sections.

Use [powder-actuated fasteners] [or] [mechanical-expansion anchors] instead of building attachments where required in concrete construction.

Use pipe positioning systems in pipe spaces behind plumbing fixtures to support supply and waste piping for plumbing fixtures.

END OF SECTION 220529